## TBEN-L4-8IOL_IN
| Connection | Assembly Instance | Size (in words)
| Input | 103 | 173
[8 empty] | Name | Base Type | Offset Byte | Offset Bit | Comment
| Description | Word Offset | Bit Offset (Word Mapping) | Bit Length | Byte Offset | Bit Offset (Byte Mapping) | Data Type | STRUCT_TBEN_Lx_8IOL_103_V1_IN | STRUCT |  |  |  | User
Module status | Module state: I/O-ASSISTANT Force Mode active | 0 | 14 | 1 | 1 | 6 | BOOL | DIAG | BOOL | 0 | 0 | Module state: Module diagnostics available
| Module state: Undervoltage V1 | 0 | 9 | 1 | 1 | 1 | BOOL | ARGEE_Active | BOOL | 0 | 1 | Module state: ARGEE program active
| Module state: Undervoltage V2 | 0 | 7 | 1 | 0 | 7 | BOOL | V2 | BOOL | 0 | 7 | Module state: Undervoltage V2
| Module state: Module diagnostics available | 0 | 0 | 1 | 0 | 0 | BOOL | V1 | BOOL | 1 | 1 | Module state: Undervoltage V1
| Module state: Internal error | 0 | 10 | 1 | 1 | 2 | BOOL | Internal_Error | BOOL | 1 | 2 | Module state: Internal error
| Module state: ARGEE program active | 0 | 1 | 1 | 0 | 1 | BOOL | FCE_Mode_Active | BOOL | 1 | 6 | Module state: I/O-ASSISTANT Force Mode active
Basic | Port 1 - IO-Link (Channel 0): DI input | 1 | 0 | 1 | 2 | 0 | BOOL | DI0 | BOOL | 2 | 0 | Digital Input 0
| Port 1 - IO-Link (Channel 0): Input values valid | 2 | 0 | 1 | 4 | 0 | BOOL | DxP1 | BOOL | 2 | 1 | Cfg Digital Channel 1
| Port 2 - IO-Link (Channel 2): DI input | 1 | 2 | 1 | 2 | 2 | BOOL | DI2 | BOOL | 2 | 2 | Digital Input 2
| Port 2 - IO-Link (Channel 2): Input values valid | 2 | 2 | 1 | 4 | 2 | BOOL | DxP3 | BOOL | 2 | 3 | Cfg Digital Channel 3
| Port 3 - IO-Link (Channel 4): DI input | 1 | 4 | 1 | 2 | 4 | BOOL | DI4 | BOOL | 2 | 4 | Digital Input 4
| Port 3 - IO-Link (Channel 4): Input values valid | 2 | 4 | 1 | 4 | 4 | BOOL | DxP5 | BOOL | 2 | 5 | Cfg Digital Channel 5
| Port 4 - IO-Link (Channel 6): DI input | 1 | 6 | 1 | 2 | 6 | BOOL | DI6 | BOOL | 2 | 6 | Digital Input 6
| Port 4 - IO-Link (Channel 6): Input values valid | 2 | 6 | 1 | 4 | 6 | BOOL | DxP7 | BOOL | 2 | 7 | Cfg Digital Channel 7
| Port 5 - IO-Link (Channel 8): DI input | 1 | 8 | 1 | 3 | 0 | BOOL | DI8 | BOOL | 3 | 0 | Digital Input 8
| Port 5 - IO-Link (Channel 8): Input values valid | 2 | 8 | 1 | 5 | 0 | BOOL | DI10 | BOOL | 3 | 2 | Digital Input 10
| Port 6 - IO-Link (Channel 10): DI input | 1 | 10 | 1 | 3 | 2 | BOOL | DI12 | BOOL | 3 | 4 | Digital Input 12
| Port 6 - IO-Link (Channel 10): Input values valid | 2 | 10 | 1 | 5 | 2 | BOOL | DI14 | BOOL | 3 | 6 | Digital Input 14
| Port 7 - IO-Link (Channel 12): DI input | 1 | 12 | 1 | 3 | 4 | BOOL | DVS0 | BOOL | 4 | 0 | IO-Link Port1 Ch.0: Process Input Data Valid
| Port 7 - IO-Link (Channel 12): Input values valid | 2 | 12 | 1 | 5 | 4 | BOOL | DVS1 | BOOL | 4 | 2 | IO-Link Port2 Ch.2: Process Input Data Valid
| Port 8 - IO-Link (Channel 14): DI input | 1 | 14 | 1 | 3 | 6 | BOOL | DVS2 | BOOL | 4 | 4 | IO-Link Port3 Ch.4: Process Input Data Valid
| Port 8 - IO-Link (Channel 14): Input values valid | 2 | 14 | 1 | 5 | 6 | BOOL | DVS3 | BOOL | 4 | 6 | IO-Link Port4 Ch.6: Process Input Data Valid
| DXP channel 1: Input value | 1 | 1 | 1 | 2 | 1 | BOOL | DVS4 | BOOL | 5 | 0 | IO-Link Port5 Ch.8: Process Input Data Valid
| DXP channel 3: Input value | 1 | 3 | 1 | 2 | 3 | BOOL | DVS5 | BOOL | 5 | 2 | IO-Link Port6 Ch.10: Process Input Data Valid
| DXP channel 5: Input value | 1 | 5 | 1 | 2 | 5 | BOOL | DVS6 | BOOL | 5 | 4 | IO-Link Port7 Ch.12: Process Input Data Valid
| DXP channel 7: Input value | 1 | 7 | 1 | 2 | 7 | BOOL | DVS7 | BOOL | 5 | 6 | IO-Link Port8 Ch.14: Process Input Data Valid
Port 1 - IO-Link (Channel 0) | IO-Link port: Input data word 0 | 3 | 0 | 16 | 6 | 0 | WORD | IOL1_W0_In | WORD | 6 |  | IO-Link port: Input data word 0
| IO-Link port: Input data word 1 | 4 | 0 | 16 | 8 | 0 | WORD | IOL1_W1_In | WORD | 8 |  | IO-Link port: Input data word 1
| IO-Link port: Input data word 2 | 5 | 0 | 16 | 10 | 0 | WORD | IOL1_W2_In | WORD | 10 |  | IO-Link port: Input data word 2
| IO-Link port: Input data word 3 | 6 | 0 | 16 | 12 | 0 | WORD | IOL1_W3_In | WORD | 12 |  | IO-Link port: Input data word 3
| IO-Link port: Input data word 4 | 7 | 0 | 16 | 14 | 0 | WORD | IOL1_W4_In | WORD | 14 |  | IO-Link port: Input data word 4
| IO-Link port: Input data word 5 | 8 | 0 | 16 | 16 | 0 | WORD | IOL1_W5_In | WORD | 16 |  | IO-Link port: Input data word 5
| IO-Link port: Input data word 6 | 9 | 0 | 16 | 18 | 0 | WORD | IOL1_W6_In | WORD | 18 |  | IO-Link port: Input data word 6
| IO-Link port: Input data word 7 | 10 | 0 | 16 | 20 | 0 | WORD | IOL1_W7_In | WORD | 20 |  | IO-Link port: Input data word 7
| IO-Link port: Input data word 8 | 11 | 0 | 16 | 22 | 0 | WORD | IOL1_W8_In | WORD | 22 |  | IO-Link port: Input data word 8
| IO-Link port: Input data word 9 | 12 | 0 | 16 | 24 | 0 | WORD | IOL1_W9_In | WORD | 24 |  | IO-Link port: Input data word 9
| IO-Link port: Input data word 10 | 13 | 0 | 16 | 26 | 0 | WORD | IOL1_W10_In | WORD | 26 |  | IO-Link port: Input data word 10
| IO-Link port: Input data word 11 | 14 | 0 | 16 | 28 | 0 | WORD | IOL1_W11_In | WORD | 28 |  | IO-Link port: Input data word 11
| IO-Link port: Input data word 12 | 15 | 0 | 16 | 30 | 0 | WORD | IOL1_W12_In | WORD | 30 |  | IO-Link port: Input data word 12
| IO-Link port: Input data word 13 | 16 | 0 | 16 | 32 | 0 | WORD | IOL1_W13_In | WORD | 32 |  | IO-Link port: Input data word 13
| IO-Link port: Input data word 14 | 17 | 0 | 16 | 34 | 0 | WORD | IOL1_W14_In | WORD | 34 |  | IO-Link port: Input data word 14
| IO-Link port: Input data word 15 | 18 | 0 | 16 | 36 | 0 | WORD | IOL1_W15_In | WORD | 36 |  | IO-Link port: Input data word 15
Port 2 - IO-Link (Channel 2) | IO-Link port: Input data word 0 | 19 | 0 | 16 | 38 | 0 | WORD | IOL2_W0_In | WORD | 38 |  | IO-Link port: Input data word 0
| IO-Link port: Input data word 1 | 20 | 0 | 16 | 40 | 0 | WORD | IOL2_W1_In | WORD | 40 |  | IO-Link port: Input data word 1
| IO-Link port: Input data word 2 | 21 | 0 | 16 | 42 | 0 | WORD | IOL2_W2_In | WORD | 42 |  | IO-Link port: Input data word 2
| IO-Link port: Input data word 3 | 22 | 0 | 16 | 44 | 0 | WORD | IOL2_W3_In | WORD | 44 |  | IO-Link port: Input data word 3
| IO-Link port: Input data word 4 | 23 | 0 | 16 | 46 | 0 | WORD | IOL2_W4_In | WORD | 46 |  | IO-Link port: Input data word 4
| IO-Link port: Input data word 5 | 24 | 0 | 16 | 48 | 0 | WORD | IOL2_W5_In | WORD | 48 |  | IO-Link port: Input data word 5
| IO-Link port: Input data word 6 | 25 | 0 | 16 | 50 | 0 | WORD | IOL2_W6_In | WORD | 50 |  | IO-Link port: Input data word 6
| IO-Link port: Input data word 7 | 26 | 0 | 16 | 52 | 0 | WORD | IOL2_W7_In | WORD | 52 |  | IO-Link port: Input data word 7
| IO-Link port: Input data word 8 | 27 | 0 | 16 | 54 | 0 | WORD | IOL2_W8_In | WORD | 54 |  | IO-Link port: Input data word 8
| IO-Link port: Input data word 9 | 28 | 0 | 16 | 56 | 0 | WORD | IOL2_W9_In | WORD | 56 |  | IO-Link port: Input data word 9
| IO-Link port: Input data word 10 | 29 | 0 | 16 | 58 | 0 | WORD | IOL2_W10_In | WORD | 58 |  | IO-Link port: Input data word 10
| IO-Link port: Input data word 11 | 30 | 0 | 16 | 60 | 0 | WORD | IOL2_W11_In | WORD | 60 |  | IO-Link port: Input data word 11
| IO-Link port: Input data word 12 | 31 | 0 | 16 | 62 | 0 | WORD | IOL2_W12_In | WORD | 62 |  | IO-Link port: Input data word 12
| IO-Link port: Input data word 13 | 32 | 0 | 16 | 64 | 0 | WORD | IOL2_W13_In | WORD | 64 |  | IO-Link port: Input data word 13
| IO-Link port: Input data word 14 | 33 | 0 | 16 | 66 | 0 | WORD | IOL2_W14_In | WORD | 66 |  | IO-Link port: Input data word 14
| IO-Link port: Input data word 15 | 34 | 0 | 16 | 68 | 0 | WORD | IOL2_W15_In | WORD | 68 |  | IO-Link port: Input data word 15
Port 3 - IO-Link (Channel 4) | IO-Link port: Input data word 0 | 35 | 0 | 16 | 70 | 0 | WORD | IOL3_W0_In | WORD | 70 |  | IO-Link port: Input data word 0
| IO-Link port: Input data word 1 | 36 | 0 | 16 | 72 | 0 | WORD | IOL3_W1_In | WORD | 72 |  | IO-Link port: Input data word 1
| IO-Link port: Input data word 2 | 37 | 0 | 16 | 74 | 0 | WORD | IOL3_W2_In | WORD | 74 |  | IO-Link port: Input data word 2
| IO-Link port: Input data word 3 | 38 | 0 | 16 | 76 | 0 | WORD | IOL3_W3_In | WORD | 76 |  | IO-Link port: Input data word 3
| IO-Link port: Input data word 4 | 39 | 0 | 16 | 78 | 0 | WORD | IOL3_W4_In | WORD | 78 |  | IO-Link port: Input data word 4
| IO-Link port: Input data word 5 | 40 | 0 | 16 | 80 | 0 | WORD | IOL3_W5_In | WORD | 80 |  | IO-Link port: Input data word 5
| IO-Link port: Input data word 6 | 41 | 0 | 16 | 82 | 0 | WORD | IOL3_W6_In | WORD | 82 |  | IO-Link port: Input data word 6
| IO-Link port: Input data word 7 | 42 | 0 | 16 | 84 | 0 | WORD | IOL3_W7_In | WORD | 84 |  | IO-Link port: Input data word 7
| IO-Link port: Input data word 8 | 43 | 0 | 16 | 86 | 0 | WORD | IOL3_W8_In | WORD | 86 |  | IO-Link port: Input data word 8
| IO-Link port: Input data word 9 | 44 | 0 | 16 | 88 | 0 | WORD | IOL3_W9_In | WORD | 88 |  | IO-Link port: Input data word 9
| IO-Link port: Input data word 10 | 45 | 0 | 16 | 90 | 0 | WORD | IOL3_W10_In | WORD | 90 |  | IO-Link port: Input data word 10
| IO-Link port: Input data word 11 | 46 | 0 | 16 | 92 | 0 | WORD | IOL3_W11_In | WORD | 92 |  | IO-Link port: Input data word 11
| IO-Link port: Input data word 12 | 47 | 0 | 16 | 94 | 0 | WORD | IOL3_W12_In | WORD | 94 |  | IO-Link port: Input data word 12
| IO-Link port: Input data word 13 | 48 | 0 | 16 | 96 | 0 | WORD | IOL3_W13_In | WORD | 96 |  | IO-Link port: Input data word 13
| IO-Link port: Input data word 14 | 49 | 0 | 16 | 98 | 0 | WORD | IOL3_W14_In | WORD | 98 |  | IO-Link port: Input data word 14
| IO-Link port: Input data word 15 | 50 | 0 | 16 | 100 | 0 | WORD | IOL3_W15_In | WORD | 100 |  | IO-Link port: Input data word 15
Port 4 - IO-Link (Channel 6) | IO-Link port: Input data word 0 | 51 | 0 | 16 | 102 | 0 | WORD | IOL4_W0_In | WORD | 102 |  | IO-Link port: Input data word 0
| IO-Link port: Input data word 1 | 52 | 0 | 16 | 104 | 0 | WORD | IOL4_W1_In | WORD | 104 |  | IO-Link port: Input data word 1
| IO-Link port: Input data word 2 | 53 | 0 | 16 | 106 | 0 | WORD | IOL4_W2_In | WORD | 106 |  | IO-Link port: Input data word 2
| IO-Link port: Input data word 3 | 54 | 0 | 16 | 108 | 0 | WORD | IOL4_W3_In | WORD | 108 |  | IO-Link port: Input data word 3
| IO-Link port: Input data word 4 | 55 | 0 | 16 | 110 | 0 | WORD | IOL4_W4_In | WORD | 110 |  | IO-Link port: Input data word 4
| IO-Link port: Input data word 5 | 56 | 0 | 16 | 112 | 0 | WORD | IOL4_W5_In | WORD | 112 |  | IO-Link port: Input data word 5
| IO-Link port: Input data word 6 | 57 | 0 | 16 | 114 | 0 | WORD | IOL4_W6_In | WORD | 114 |  | IO-Link port: Input data word 6
| IO-Link port: Input data word 7 | 58 | 0 | 16 | 116 | 0 | WORD | IOL4_W7_In | WORD | 116 |  | IO-Link port: Input data word 7
| IO-Link port: Input data word 8 | 59 | 0 | 16 | 118 | 0 | WORD | IOL4_W8_In | WORD | 118 |  | IO-Link port: Input data word 8
| IO-Link port: Input data word 9 | 60 | 0 | 16 | 120 | 0 | WORD | IOL4_W9_In | WORD | 120 |  | IO-Link port: Input data word 9
| IO-Link port: Input data word 10 | 61 | 0 | 16 | 122 | 0 | WORD | IOL4_W10_In | WORD | 122 |  | IO-Link port: Input data word 10
| IO-Link port: Input data word 11 | 62 | 0 | 16 | 124 | 0 | WORD | IOL4_W11_In | WORD | 124 |  | IO-Link port: Input data word 11
| IO-Link port: Input data word 12 | 63 | 0 | 16 | 126 | 0 | WORD | IOL4_W12_In | WORD | 126 |  | IO-Link port: Input data word 12
| IO-Link port: Input data word 13 | 64 | 0 | 16 | 128 | 0 | WORD | IOL4_W13_In | WORD | 128 |  | IO-Link port: Input data word 13
| IO-Link port: Input data word 14 | 65 | 0 | 16 | 130 | 0 | WORD | IOL4_W14_In | WORD | 130 |  | IO-Link port: Input data word 14
| IO-Link port: Input data word 15 | 66 | 0 | 16 | 132 | 0 | WORD | IOL4_W15_In | WORD | 132 |  | IO-Link port: Input data word 15
Port 5 - IO-Link (Channel 8) | IO-Link port: Input data word 0 | 67 | 0 | 16 | 134 | 0 | WORD | IOL5_W0_In | WORD | 134 |  | IO-Link port: Input data word 0
| IO-Link port: Input data word 1 | 68 | 0 | 16 | 136 | 0 | WORD | IOL5_W1_In | WORD | 136 |  | IO-Link port: Input data word 1
| IO-Link port: Input data word 2 | 69 | 0 | 16 | 138 | 0 | WORD | IOL5_W2_In | WORD | 138 |  | IO-Link port: Input data word 2
| IO-Link port: Input data word 3 | 70 | 0 | 16 | 140 | 0 | WORD | IOL5_W3_In | WORD | 140 |  | IO-Link port: Input data word 3
| IO-Link port: Input data word 4 | 71 | 0 | 16 | 142 | 0 | WORD | IOL5_W4_In | WORD | 142 |  | IO-Link port: Input data word 4
| IO-Link port: Input data word 5 | 72 | 0 | 16 | 144 | 0 | WORD | IOL5_W5_In | WORD | 144 |  | IO-Link port: Input data word 5
| IO-Link port: Input data word 6 | 73 | 0 | 16 | 146 | 0 | WORD | IOL5_W6_In | WORD | 146 |  | IO-Link port: Input data word 6
| IO-Link port: Input data word 7 | 74 | 0 | 16 | 148 | 0 | WORD | IOL5_W7_In | WORD | 148 |  | IO-Link port: Input data word 7
| IO-Link port: Input data word 8 | 75 | 0 | 16 | 150 | 0 | WORD | IOL5_W8_In | WORD | 150 |  | IO-Link port: Input data word 8
| IO-Link port: Input data word 9 | 76 | 0 | 16 | 152 | 0 | WORD | IOL5_W9_In | WORD | 152 |  | IO-Link port: Input data word 9
| IO-Link port: Input data word 10 | 77 | 0 | 16 | 154 | 0 | WORD | IOL5_W10_In | WORD | 154 |  | IO-Link port: Input data word 10
| IO-Link port: Input data word 11 | 78 | 0 | 16 | 156 | 0 | WORD | IOL5_W11_In | WORD | 156 |  | IO-Link port: Input data word 11
| IO-Link port: Input data word 12 | 79 | 0 | 16 | 158 | 0 | WORD | IOL5_W12_In | WORD | 158 |  | IO-Link port: Input data word 12
| IO-Link port: Input data word 13 | 80 | 0 | 16 | 160 | 0 | WORD | IOL5_W13_In | WORD | 160 |  | IO-Link port: Input data word 13
| IO-Link port: Input data word 14 | 81 | 0 | 16 | 162 | 0 | WORD | IOL5_W14_In | WORD | 162 |  | IO-Link port: Input data word 14
| IO-Link port: Input data word 15 | 82 | 0 | 16 | 164 | 0 | WORD | IOL5_W15_In | WORD | 164 |  | IO-Link port: Input data word 15
Port 6 - IO-Link (Channel 10) | IO-Link port: Input data word 0 | 83 | 0 | 16 | 166 | 0 | WORD | IOL6_W0_In | WORD | 166 |  | IO-Link port: Input data word 0
| IO-Link port: Input data word 1 | 84 | 0 | 16 | 168 | 0 | WORD | IOL6_W1_In | WORD | 168 |  | IO-Link port: Input data word 1
| IO-Link port: Input data word 2 | 85 | 0 | 16 | 170 | 0 | WORD | IOL6_W2_In | WORD | 170 |  | IO-Link port: Input data word 2
| IO-Link port: Input data word 3 | 86 | 0 | 16 | 172 | 0 | WORD | IOL6_W3_In | WORD | 172 |  | IO-Link port: Input data word 3
| IO-Link port: Input data word 4 | 87 | 0 | 16 | 174 | 0 | WORD | IOL6_W4_In | WORD | 174 |  | IO-Link port: Input data word 4
| IO-Link port: Input data word 5 | 88 | 0 | 16 | 176 | 0 | WORD | IOL6_W5_In | WORD | 176 |  | IO-Link port: Input data word 5
| IO-Link port: Input data word 6 | 89 | 0 | 16 | 178 | 0 | WORD | IOL6_W6_In | WORD | 178 |  | IO-Link port: Input data word 6
| IO-Link port: Input data word 7 | 90 | 0 | 16 | 180 | 0 | WORD | IOL6_W7_In | WORD | 180 |  | IO-Link port: Input data word 7
| IO-Link port: Input data word 8 | 91 | 0 | 16 | 182 | 0 | WORD | IOL6_W8_In | WORD | 182 |  | IO-Link port: Input data word 8
| IO-Link port: Input data word 9 | 92 | 0 | 16 | 184 | 0 | WORD | IOL6_W9_In | WORD | 184 |  | IO-Link port: Input data word 9
| IO-Link port: Input data word 10 | 93 | 0 | 16 | 186 | 0 | WORD | IOL6_W10_In | WORD | 186 |  | IO-Link port: Input data word 10
| IO-Link port: Input data word 11 | 94 | 0 | 16 | 188 | 0 | WORD | IOL6_W11_In | WORD | 188 |  | IO-Link port: Input data word 11
| IO-Link port: Input data word 12 | 95 | 0 | 16 | 190 | 0 | WORD | IOL6_W12_In | WORD | 190 |  | IO-Link port: Input data word 12
| IO-Link port: Input data word 13 | 96 | 0 | 16 | 192 | 0 | WORD | IOL6_W13_In | WORD | 192 |  | IO-Link port: Input data word 13
| IO-Link port: Input data word 14 | 97 | 0 | 16 | 194 | 0 | WORD | IOL6_W14_In | WORD | 194 |  | IO-Link port: Input data word 14
| IO-Link port: Input data word 15 | 98 | 0 | 16 | 196 | 0 | WORD | IOL6_W15_In | WORD | 196 |  | IO-Link port: Input data word 15
Port 7 - IO-Link (Channel 12) | IO-Link port: Input data word 0 | 99 | 0 | 16 | 198 | 0 | WORD | IOL7_W0_In | WORD | 198 |  | IO-Link port: Input data word 0
| IO-Link port: Input data word 1 | 100 | 0 | 16 | 200 | 0 | WORD | IOL7_W1_In | WORD | 200 |  | IO-Link port: Input data word 1
| IO-Link port: Input data word 2 | 101 | 0 | 16 | 202 | 0 | WORD | IOL7_W2_In | WORD | 202 |  | IO-Link port: Input data word 2
| IO-Link port: Input data word 3 | 102 | 0 | 16 | 204 | 0 | WORD | IOL7_W3_In | WORD | 204 |  | IO-Link port: Input data word 3
| IO-Link port: Input data word 4 | 103 | 0 | 16 | 206 | 0 | WORD | IOL7_W4_In | WORD | 206 |  | IO-Link port: Input data word 4
| IO-Link port: Input data word 5 | 104 | 0 | 16 | 208 | 0 | WORD | IOL7_W5_In | WORD | 208 |  | IO-Link port: Input data word 5
| IO-Link port: Input data word 6 | 105 | 0 | 16 | 210 | 0 | WORD | IOL7_W6_In | WORD | 210 |  | IO-Link port: Input data word 6
| IO-Link port: Input data word 7 | 106 | 0 | 16 | 212 | 0 | WORD | IOL7_W7_In | WORD | 212 |  | IO-Link port: Input data word 7
| IO-Link port: Input data word 8 | 107 | 0 | 16 | 214 | 0 | WORD | IOL7_W8_In | WORD | 214 |  | IO-Link port: Input data word 8
| IO-Link port: Input data word 9 | 108 | 0 | 16 | 216 | 0 | WORD | IOL7_W9_In | WORD | 216 |  | IO-Link port: Input data word 9
| IO-Link port: Input data word 10 | 109 | 0 | 16 | 218 | 0 | WORD | IOL7_W10_In | WORD | 218 |  | IO-Link port: Input data word 10
| IO-Link port: Input data word 11 | 110 | 0 | 16 | 220 | 0 | WORD | IOL7_W11_In | WORD | 220 |  | IO-Link port: Input data word 11
| IO-Link port: Input data word 12 | 111 | 0 | 16 | 222 | 0 | WORD | IOL7_W12_In | WORD | 222 |  | IO-Link port: Input data word 12
| IO-Link port: Input data word 13 | 112 | 0 | 16 | 224 | 0 | WORD | IOL7_W13_In | WORD | 224 |  | IO-Link port: Input data word 13
| IO-Link port: Input data word 14 | 113 | 0 | 16 | 226 | 0 | WORD | IOL7_W14_In | WORD | 226 |  | IO-Link port: Input data word 14
| IO-Link port: Input data word 15 | 114 | 0 | 16 | 228 | 0 | WORD | IOL7_W15_In | WORD | 228 |  | IO-Link port: Input data word 15
Port 8 - IO-Link (Channel 14) | IO-Link port: Input data word 0 | 115 | 0 | 16 | 230 | 0 | WORD | IOL8_W0_In | WORD | 230 |  | IO-Link port: Input data word 0
| IO-Link port: Input data word 1 | 116 | 0 | 16 | 232 | 0 | WORD | IOL8_W1_In | WORD | 232 |  | IO-Link port: Input data word 1
| IO-Link port: Input data word 2 | 117 | 0 | 16 | 234 | 0 | WORD | IOL8_W2_In | WORD | 234 |  | IO-Link port: Input data word 2
| IO-Link port: Input data word 3 | 118 | 0 | 16 | 236 | 0 | WORD | IOL8_W3_In | WORD | 236 |  | IO-Link port: Input data word 3
| IO-Link port: Input data word 4 | 119 | 0 | 16 | 238 | 0 | WORD | IOL8_W4_In | WORD | 238 |  | IO-Link port: Input data word 4
| IO-Link port: Input data word 5 | 120 | 0 | 16 | 240 | 0 | WORD | IOL8_W5_In | WORD | 240 |  | IO-Link port: Input data word 5
| IO-Link port: Input data word 6 | 121 | 0 | 16 | 242 | 0 | WORD | IOL8_W6_In | WORD | 242 |  | IO-Link port: Input data word 6
| IO-Link port: Input data word 7 | 122 | 0 | 16 | 244 | 0 | WORD | IOL8_W7_In | WORD | 244 |  | IO-Link port: Input data word 7
| IO-Link port: Input data word 8 | 123 | 0 | 16 | 246 | 0 | WORD | IOL8_W8_In | WORD | 246 |  | IO-Link port: Input data word 8
| IO-Link port: Input data word 9 | 124 | 0 | 16 | 248 | 0 | WORD | IOL8_W9_In | WORD | 248 |  | IO-Link port: Input data word 9
| IO-Link port: Input data word 10 | 125 | 0 | 16 | 250 | 0 | WORD | IOL8_W10_In | WORD | 250 |  | IO-Link port: Input data word 10
| IO-Link port: Input data word 11 | 126 | 0 | 16 | 252 | 0 | WORD | IOL8_W11_In | WORD | 252 |  | IO-Link port: Input data word 11
| IO-Link port: Input data word 12 | 127 | 0 | 16 | 254 | 0 | WORD | IOL8_W12_In | WORD | 254 |  | IO-Link port: Input data word 12
| IO-Link port: Input data word 13 | 128 | 0 | 16 | 256 | 0 | WORD | IOL8_W13_In | WORD | 256 |  | IO-Link port: Input data word 13
| IO-Link port: Input data word 14 | 129 | 0 | 16 | 258 | 0 | WORD | IOL8_W14_In | WORD | 258 |  | IO-Link port: Input data word 14
| IO-Link port: Input data word 15 | 130 | 0 | 16 | 260 | 0 | WORD | IOL8_W15_In | WORD | 260 |  | IO-Link port: Input data word 15
Diagnostics | Group diagnosis: Overcurrent VAUX1 Pin1 C0 (Ch0/1) | 131 | 0 | 1 | 262 | 0 | BOOL | Pin1_C0_OverrCurr_V1 | BOOL | 262 | 0 | Group diagnosis: Overcurrent VAUX1 Pin1 C0 (Ch0/1)
| Group diagnosis: Overcurrent VAUX1 Pin1 C1 (Ch2/3) | 131 | 1 | 1 | 262 | 1 | BOOL | Pin1_C1_OverrCurr_V1 | BOOL | 262 | 1 | Group diagnosis: Overcurrent VAUX1 Pin1 C1 (Ch2/3)
| Group diagnosis: Overcurrent VAUX1 Pin1 C2 (Ch4/5) | 131 | 2 | 1 | 262 | 2 | BOOL | Pin1_C2_OverrCurr_V1 | BOOL | 262 | 2 | Group diagnosis: Overcurrent VAUX1 Pin1 C2 (Ch4/5)
| Group diagnosis: Overcurrent VAUX1 Pin1 C3 (Ch6/7) | 131 | 3 | 1 | 262 | 3 | BOOL | Pin1_C3_OverrCurr_V1 | BOOL | 262 | 3 | Group diagnosis: Overcurrent VAUX1 Pin1 C3 (Ch6/7)
| Group diagnosis: Overcurrent VAUX1 Pin1 C4 (Ch8) | 131 | 4 | 1 | 262 | 4 | BOOL | Pin1_C4_OverrCurr_V1 | BOOL | 262 | 4 | Group diagnosis: Overcurrent VAUX1 Pin1 C4 (Ch8)
| Group diagnosis: Overcurrent VAUX2 Pin2 C4 (Ch9) | 131 | 12 | 1 | 263 | 4 | BOOL | Pin1_C5_OverrCurr_V1 | BOOL | 262 | 5 | Group diagnosis: Overcurrent VAUX1 Pin1 C5 (Ch10)
| Group diagnosis: Overcurrent VAUX1 Pin1 C5 (Ch10) | 131 | 5 | 1 | 262 | 5 | BOOL | Pin1_C6_OverrCurr_V1 | BOOL | 262 | 6 | Group diagnosis: Overcurrent VAUX1 Pin1 C6 (Ch12)
| Group diagnosis: Overcurrent VAUX2 Pin2 C5 (Ch11) | 131 | 13 | 1 | 263 | 5 | BOOL | Pin1_C7_OverrCurr_V1 | BOOL | 262 | 7 | Group diagnosis: Overcurrent VAUX1 Pin1 C7 (Ch14)
| Group diagnosis: Overcurrent VAUX1 Pin1 C6 (Ch12) | 131 | 6 | 1 | 262 | 6 | BOOL | Pin2_C4_OverrCurr_V2 | BOOL | 263 | 4 | Group diagnosis: Overcurrent VAUX2 Pin2 C4 (Ch9)
| Group diagnosis: Overcurrent VAUX2 Pin2 C6 (Ch13) | 131 | 14 | 1 | 263 | 6 | BOOL | Pin2_C5_OverrCurr_V2 | BOOL | 263 | 5 | Group diagnosis: Overcurrent VAUX2 Pin2 C5 (Ch11)
| Group diagnosis: Overcurrent VAUX1 Pin1 C7 (Ch14) | 131 | 7 | 1 | 262 | 7 | BOOL | Pin2_C6_OverrCurr_V2 | BOOL | 263 | 6 | Group diagnosis: Overcurrent VAUX2 Pin2 C6 (Ch13)
| Group diagnosis: Overcurrent VAUX2 Pin2 C7 (Ch15) | 131 | 15 | 1 | 263 | 7 | BOOL | Pin2_C7_OverrCurr_V2 | BOOL | 263 | 7 | Group diagnosis: Overcurrent VAUX2 Pin2 C7 (Ch15)
| DXP channel 1: Overcurrent output | 132 | 1 | 1 | 264 | 1 | BOOL | DxP1_OverrCurr | BOOL | 264 | 1 | DXP channel 1: Overcurrent output
| DXP channel 3: Overcurrent output | 132 | 3 | 1 | 264 | 3 | BOOL | DxP3_OverrCurr | BOOL | 264 | 3 | DXP channel 3: Overcurrent output
| DXP channel 5: Overcurrent output | 132 | 5 | 1 | 264 | 5 | BOOL | DxP5_OverrCurr | BOOL | 264 | 5 | DXP channel 5: Overcurrent output
| DXP channel 7: Overcurrent output | 132 | 7 | 1 | 264 | 7 | BOOL | DxP7_OverrCurr | BOOL | 264 | 7 | DXP channel 7: Overcurrent output
| IO-Link channel 0: Wrong or missing device | 133 | 2 | 1 | 266 | 2 | BOOL | IOL1_Port_Param_Err | BOOL | 266 | 1 | IO-Link channel 0: Port parameterization error
| IO-Link channel 0: Data storage error | 133 | 3 | 1 | 266 | 3 | BOOL | IOL1_Wrong_Missing | BOOL | 266 | 2 | IO-Link channel 0: Wrong or missing device
| IO-Link channel 0: Process input data invalid | 133 | 5 | 1 | 266 | 5 | BOOL | IOL1_Data_St_Err | BOOL | 266 | 3 | IO-Link channel 0: Data storage error
| IO-Link channel 0: Hardware error | 133 | 4 | 1 | 266 | 4 | BOOL | IOL1_HW_Err | BOOL | 266 | 4 | IO-Link channel 0: Process input data invalid
| IO-Link channel 0: Maintenance events | 133 | 6 | 1 | 266 | 6 | BOOL | IOL1_Proc_Dat_Invalid | BOOL | 266 | 5 | IO-Link channel 0: Hardware error
| IO-Link channel 0: Out of specification error | 133 | 7 | 1 | 266 | 7 | BOOL | IOL1_Maint_Evts | BOOL | 266 | 6 | IO-Link channel 0: Maintenance events
| IO-Link channel 0: Parameterization error | 133 | 8 | 1 | 267 | 0 | BOOL | IOL1_Out_Spec_Err | BOOL | 266 | 7 | IO-Link channel 0: Out of specification error
| IO-Link channel 0: Overtemperature | 133 | 9 | 1 | 267 | 1 | BOOL | IOL1_Param_Err | BOOL | 267 | 0 | IO-Link channel 0: Parameterization error
| IO-Link channel 0: Overtemperature | 133 | 9 | 1 | 267 | 1 | BOOL | IOL1_OverTemp | BOOL | 267 | 1 | IO-Link channel 0: Overtemperature
| IO-Link channel 0: Lower limit value underrun | 133 | 10 | 1 | 267 | 2 | BOOL | IOL1_Under_LL | BOOL | 267 | 2 | IO-Link channel 0: Lower limit value underrun
| IO-Link channel 0: Upper limit value exceeded | 133 | 11 | 1 | 267 | 3 | BOOL | IOL1_Over_UL | BOOL | 267 | 3 | IO-Link channel 0: Upper limit value exceeded
| IO-Link channel 0: Undervoltage | 133 | 12 | 1 | 267 | 4 | BOOL | IOL1_V_LOW | BOOL | 267 | 4 | IO-Link channel 0: Undervoltage
| IO-Link channel 0: Overvoltage | 133 | 13 | 1 | 267 | 5 | BOOL | IOL1_V_HIGH | BOOL | 267 | 5 | IO-Link channel 0: Overvoltage
| IO-Link channel 0: Overload | 133 | 14 | 1 | 267 | 6 | BOOL | IOL1_OL | BOOL | 267 | 6 | IO-Link channel 0: Overload
| IO-Link channel 0: Common error | 133 | 15 | 1 | 267 | 7 | BOOL | IOL1_Cmd_Err | BOOL | 267 | 7 | IO-Link channel 0: Common error
| IO-Link channel 0: Port parameterization error | 133 | 1 | 1 | 266 | 1 | BOOL | IOL2_Port_Param_Err | BOOL | 268 | 1 | IO-Link channel 2: Port parameterization error
| IO-Link channel 2: Wrong or missing device | 134 | 2 | 1 | 268 | 2 | BOOL | IOL2_Wrong_Missing | BOOL | 268 | 2 | IO-Link channel 2: Wrong or missing device
| IO-Link channel 2: Data storage error | 134 | 3 | 1 | 268 | 3 | BOOL | IOL2_Data_St_Err | BOOL | 268 | 3 | IO-Link channel 2: Data storage error
| IO-Link channel 2: Process input data invalid | 134 | 5 | 1 | 268 | 5 | BOOL | IOL2_HW_Err | BOOL | 268 | 4 | IO-Link channel 2: Process input data invalid
| IO-Link channel 2: Hardware error | 134 | 4 | 1 | 268 | 4 | BOOL | IOL2_Proc_Dat_Invalid | BOOL | 268 | 5 | IO-Link channel 2: Hardware error
| IO-Link channel 2: Maintenance events | 134 | 6 | 1 | 268 | 6 | BOOL | IOL2_Maint_Evts | BOOL | 268 | 6 | IO-Link channel 2: Maintenance events
| IO-Link channel 2: Out of specification error | 134 | 7 | 1 | 268 | 7 | BOOL | IOL2_Out_Spec_Err | BOOL | 268 | 7 | IO-Link channel 2: Out of specification error
| IO-Link channel 2: Parameterization error | 134 | 8 | 1 | 269 | 0 | BOOL | IOL2_Param_Err | BOOL | 269 | 0 | IO-Link channel 2: Parameterization error
| IO-Link channel 2: Overtemperature | 134 | 9 | 1 | 269 | 1 | BOOL | IOL2_OverTemp | BOOL | 269 | 1 | IO-Link channel 2: Overtemperature
| IO-Link channel 2: Overtemperature | 134 | 9 | 1 | 269 | 1 | BOOL | IOL2_Under_LL | BOOL | 269 | 2 | IO-Link channel 2: Lower limit value underrun
| IO-Link channel 2: Lower limit value underrun | 134 | 10 | 1 | 269 | 2 | BOOL | IOL2_Over_UL | BOOL | 269 | 3 | IO-Link channel 2: Upper limit value exceeded
| IO-Link channel 2: Upper limit value exceeded | 134 | 11 | 1 | 269 | 3 | BOOL | IOL2_V_LOW | BOOL | 269 | 4 | IO-Link channel 2: Undervoltage
| IO-Link channel 2: Undervoltage | 134 | 12 | 1 | 269 | 4 | BOOL | IOL2_V_HIGH | BOOL | 269 | 5 | IO-Link channel 2: Overvoltage
| IO-Link channel 2: Overvoltage | 134 | 13 | 1 | 269 | 5 | BOOL | IOL2_OL | BOOL | 269 | 6 | IO-Link channel 2: Overload
| IO-Link channel 2: Overload | 134 | 14 | 1 | 269 | 6 | BOOL | IOL2_Cmd_Err | BOOL | 269 | 7 | IO-Link channel 2: Common error
| IO-Link channel 2: Common error | 134 | 15 | 1 | 269 | 7 | BOOL | IOL3_Port_Param_Err | BOOL | 270 | 1 | IO-Link channel 4: Port parameterization error
| IO-Link channel 2: Port parameterization error | 134 | 1 | 1 | 268 | 1 | BOOL | IOL3_Wrong_Missing | BOOL | 270 | 2 | IO-Link channel 4: Wrong or missing device
| IO-Link channel 4: Wrong or missing device | 135 | 2 | 1 | 270 | 2 | BOOL | IOL3_Data_St_Err | BOOL | 270 | 3 | IO-Link channel 4: Data storage error
| IO-Link channel 4: Data storage error | 135 | 3 | 1 | 270 | 3 | BOOL | IOL3_HW_Err | BOOL | 270 | 4 | IO-Link channel 4: Process input data invalid
| IO-Link channel 4: Process input data invalid | 135 | 5 | 1 | 270 | 5 | BOOL | IOL3_Proc_Dat_Invalid | BOOL | 270 | 5 | IO-Link channel 4: Hardware error
| IO-Link channel 4: Hardware error | 135 | 4 | 1 | 270 | 4 | BOOL | IOL3_Maint_Evts | BOOL | 270 | 6 | IO-Link channel 4: Maintenance events
| IO-Link channel 4: Maintenance events | 135 | 6 | 1 | 270 | 6 | BOOL | IOL3_Out_Spec_Err | BOOL | 270 | 7 | IO-Link channel 4: Out of specification error
| IO-Link channel 4: Out of specification error | 135 | 7 | 1 | 270 | 7 | BOOL | IOL3_Param_Err | BOOL | 271 | 0 | IO-Link channel 4: Parameterization error
| IO-Link channel 4: Parameterization error | 135 | 8 | 1 | 271 | 0 | BOOL | IOL3_OverTemp | BOOL | 271 | 1 | IO-Link channel 4: Overtemperature
| IO-Link channel 4: Overtemperature | 135 | 9 | 1 | 271 | 1 | BOOL | IOL3_Under_LL | BOOL | 271 | 2 | IO-Link channel 4: Lower limit value underrun
| IO-Link channel 4: Overtemperature | 135 | 9 | 1 | 271 | 1 | BOOL | IOL3_Over_UL | BOOL | 271 | 3 | IO-Link channel 4: Upper limit value exceeded
| IO-Link channel 4: Lower limit value underrun | 135 | 10 | 1 | 271 | 2 | BOOL | IOL3_V_LOW | BOOL | 271 | 4 | IO-Link channel 4: Undervoltage
| IO-Link channel 4: Upper limit value exceeded | 135 | 11 | 1 | 271 | 3 | BOOL | IOL3_V_HIGH | BOOL | 271 | 5 | IO-Link channel 4: Overvoltage
| IO-Link channel 4: Undervoltage | 135 | 12 | 1 | 271 | 4 | BOOL | IOL3_OL | BOOL | 271 | 6 | IO-Link channel 4: Overload
| IO-Link channel 4: Overvoltage | 135 | 13 | 1 | 271 | 5 | BOOL | IOL3_Cmd_Err | BOOL | 271 | 7 | IO-Link channel 4: Common error
| IO-Link channel 4: Overload | 135 | 14 | 1 | 271 | 6 | BOOL | IOL4_Port_Param_Err | BOOL | 272 | 1 | IO-Link channel 6: Port parameterization error
| IO-Link channel 4: Common error | 135 | 15 | 1 | 271 | 7 | BOOL | IOL4_Wrong_Missing | BOOL | 272 | 2 | IO-Link channel 6: Wrong or missing device
| IO-Link channel 4: Port parameterization error | 135 | 1 | 1 | 270 | 1 | BOOL | IOL4_Data_St_Err | BOOL | 272 | 3 | IO-Link channel 6: Data storage error
| IO-Link channel 6: Wrong or missing device | 136 | 2 | 1 | 272 | 2 | BOOL | IOL4_HW_Err | BOOL | 272 | 4 | IO-Link channel 6: Process input data invalid
| IO-Link channel 6: Data storage error | 136 | 3 | 1 | 272 | 3 | BOOL | IOL4_Proc_Dat_Invalid | BOOL | 272 | 5 | IO-Link channel 6: Hardware error
| IO-Link channel 6: Process input data invalid | 136 | 5 | 1 | 272 | 5 | BOOL | IOL4_Maint_Evts | BOOL | 272 | 6 | IO-Link channel 6: Maintenance events
| IO-Link channel 6: Hardware error | 136 | 4 | 1 | 272 | 4 | BOOL | IOL4_Out_Spec_Err | BOOL | 272 | 7 | IO-Link channel 6: Out of specification error
| IO-Link channel 6: Maintenance events | 136 | 6 | 1 | 272 | 6 | BOOL | IOL4_Param_Err | BOOL | 273 | 0 | IO-Link channel 6: Parameterization error
| IO-Link channel 6: Out of specification error | 136 | 7 | 1 | 272 | 7 | BOOL | IOL4_OverTemp | BOOL | 273 | 1 | IO-Link channel 6: Overtemperature
| IO-Link channel 6: Parameterization error | 136 | 8 | 1 | 273 | 0 | BOOL | IOL4_Under_LL | BOOL | 273 | 2 | IO-Link channel 6: Lower limit value underrun
| IO-Link channel 6: Overtemperature | 136 | 9 | 1 | 273 | 1 | BOOL | IOL4_Over_UL | BOOL | 273 | 3 | IO-Link channel 6: Upper limit value exceeded
| IO-Link channel 6: Overtemperature | 136 | 9 | 1 | 273 | 1 | BOOL | IOL4_V_LOW | BOOL | 273 | 4 | IO-Link channel 6: Undervoltage
| IO-Link channel 6: Lower limit value underrun | 136 | 10 | 1 | 273 | 2 | BOOL | IOL4_V_HIGH | BOOL | 273 | 5 | IO-Link channel 6: Overvoltage
| IO-Link channel 6: Upper limit value exceeded | 136 | 11 | 1 | 273 | 3 | BOOL | IOL4_OL | BOOL | 273 | 6 | IO-Link channel 6: Overload
| IO-Link channel 6: Undervoltage | 136 | 12 | 1 | 273 | 4 | BOOL | IOL4_Cmd_Err | BOOL | 273 | 7 | IO-Link channel 6: Common error
| IO-Link channel 6: Overvoltage | 136 | 13 | 1 | 273 | 5 | BOOL | IOL5_Port_Param_Err | BOOL | 274 | 1 | IO-Link channel 8: Port parameterization error
| IO-Link channel 6: Overload | 136 | 14 | 1 | 273 | 6 | BOOL | IOL5_Wrong_Missing | BOOL | 274 | 2 | IO-Link channel 8: Wrong or missing device
| IO-Link channel 6: Common error | 136 | 15 | 1 | 273 | 7 | BOOL | IOL5_Data_St_Err | BOOL | 274 | 3 | IO-Link channel 8: Data storage error
| IO-Link channel 6: Port parameterization error | 136 | 1 | 1 | 272 | 1 | BOOL | IOL5_HW_Err | BOOL | 274 | 4 | IO-Link channel 8: Process input data invalid
| IO-Link channel 8: Wrong or missing device | 137 | 2 | 1 | 274 | 2 | BOOL | IOL5_Proc_Dat_Invalid | BOOL | 274 | 5 | IO-Link channel 8: Hardware error
| IO-Link channel 8: Data storage error | 137 | 3 | 1 | 274 | 3 | BOOL | IOL5_Maint_Evts | BOOL | 274 | 6 | IO-Link channel 8: Maintenance events
| IO-Link channel 8: Process input data invalid | 137 | 5 | 1 | 274 | 5 | BOOL | IOL5_Out_Spec_Err | BOOL | 274 | 7 | IO-Link channel 8: Out of specification error
| IO-Link channel 8: Hardware error | 137 | 4 | 1 | 274 | 4 | BOOL | IOL5_Param_Err | BOOL | 275 | 0 | IO-Link channel 8: Parameterization error
| IO-Link channel 8: Maintenance events | 137 | 6 | 1 | 274 | 6 | BOOL | IOL5_OverTemp | BOOL | 275 | 1 | IO-Link channel 8: Overtemperature
| IO-Link channel 8: Out of specification error | 137 | 7 | 1 | 274 | 7 | BOOL | IOL5_Under_LL | BOOL | 275 | 2 | IO-Link channel 8: Lower limit value underrun
| IO-Link channel 8: Parameterization error | 137 | 8 | 1 | 275 | 0 | BOOL | IOL5_Over_UL | BOOL | 275 | 3 | IO-Link channel 8: Upper limit value exceeded
| IO-Link channel 8: Overtemperature | 137 | 9 | 1 | 275 | 1 | BOOL | IOL5_V_LOW | BOOL | 275 | 4 | IO-Link channel 8: Undervoltage
| IO-Link channel 8: Overtemperature | 137 | 9 | 1 | 275 | 1 | BOOL | IOL5_V_HIGH | BOOL | 275 | 5 | IO-Link channel 8: Overvoltage
| IO-Link channel 8: Lower limit value underrun | 137 | 10 | 1 | 275 | 2 | BOOL | IOL5_OL | BOOL | 275 | 6 | IO-Link channel 8: Overload
| IO-Link channel 8: Upper limit value exceeded | 137 | 11 | 1 | 275 | 3 | BOOL | IOL5_Cmd_Err | BOOL | 275 | 7 | IO-Link channel 8: Common error
| IO-Link channel 8: Undervoltage | 137 | 12 | 1 | 275 | 4 | BOOL | IOL6_Port_Param_Err | BOOL | 276 | 1 | IO-Link channel 10: Port parameterization error
| IO-Link channel 8: Overvoltage | 137 | 13 | 1 | 275 | 5 | BOOL | IOL6_Wrong_Missing | BOOL | 276 | 2 | IO-Link channel 10: Wrong or missing device
| IO-Link channel 8: Overload | 137 | 14 | 1 | 275 | 6 | BOOL | IOL6_Data_St_Err | BOOL | 276 | 3 | IO-Link channel 10: Data storage error
| IO-Link channel 8: Common error | 137 | 15 | 1 | 275 | 7 | BOOL | IOL6_HW_Err | BOOL | 276 | 4 | IO-Link channel 10: Process input data invalid
| IO-Link channel 8: Port parameterization error | 137 | 1 | 1 | 274 | 1 | BOOL | IOL6_Proc_Dat_Invalid | BOOL | 276 | 5 | IO-Link channel 10: Hardware error
| IO-Link channel 10: Wrong or missing device | 138 | 2 | 1 | 276 | 2 | BOOL | IOL6_Maint_Evts | BOOL | 276 | 6 | IO-Link channel 10: Maintenance events
| IO-Link channel 10: Data storage error | 138 | 3 | 1 | 276 | 3 | BOOL | IOL6_Out_Spec_Err | BOOL | 276 | 7 | IO-Link channel 10: Out of specification error
| IO-Link channel 10: Process input data invalid | 138 | 5 | 1 | 276 | 5 | BOOL | IOL6_Param_Err | BOOL | 277 | 0 | IO-Link channel 10: Parameterization error
| IO-Link channel 10: Hardware error | 138 | 4 | 1 | 276 | 4 | BOOL | IOL6_OverTemp | BOOL | 277 | 1 | IO-Link channel 10: Overtemperature
| IO-Link channel 10: Maintenance events | 138 | 6 | 1 | 276 | 6 | BOOL | IOL6_Under_LL | BOOL | 277 | 2 | IO-Link channel 10: Lower limit value underrun
| IO-Link channel 10: Out of specification error | 138 | 7 | 1 | 276 | 7 | BOOL | IOL6_Over_UL | BOOL | 277 | 3 | IO-Link channel 10: Upper limit value exceeded
| IO-Link channel 10: Parameterization error | 138 | 8 | 1 | 277 | 0 | BOOL | IOL6_V_LOW | BOOL | 277 | 4 | IO-Link channel 10: Undervoltage
| IO-Link channel 10: Overtemperature | 138 | 9 | 1 | 277 | 1 | BOOL | IOL6_V_HIGH | BOOL | 277 | 5 | IO-Link channel 10: Overvoltage
| IO-Link channel 10: Overtemperature | 138 | 9 | 1 | 277 | 1 | BOOL | IOL6_OL | BOOL | 277 | 6 | IO-Link channel 10: Overload
| IO-Link channel 10: Lower limit value underrun | 138 | 10 | 1 | 277 | 2 | BOOL | IOL6_Cmd_Err | BOOL | 277 | 7 | IO-Link channel 10: Common error
| IO-Link channel 10: Upper limit value exceeded | 138 | 11 | 1 | 277 | 3 | BOOL | IOL7_Port_Param_Err | BOOL | 278 | 1 | IO-Link channel 12: Port parameterization error
| IO-Link channel 10: Undervoltage | 138 | 12 | 1 | 277 | 4 | BOOL | IOL7_Wrong_Missing | BOOL | 278 | 2 | IO-Link channel 12: Wrong or missing device
| IO-Link channel 10: Overvoltage | 138 | 13 | 1 | 277 | 5 | BOOL | IOL7_Data_St_Err | BOOL | 278 | 3 | IO-Link channel 12: Data storage error
| IO-Link channel 10: Overload | 138 | 14 | 1 | 277 | 6 | BOOL | IOL7_HW_Err | BOOL | 278 | 4 | IO-Link channel 12: Process input data invalid
| IO-Link channel 10: Common error | 138 | 15 | 1 | 277 | 7 | BOOL | IOL7_Proc_Dat_Invalid | BOOL | 278 | 5 | IO-Link channel 12: Hardware error
| IO-Link channel 10: Port parameterization error | 138 | 1 | 1 | 276 | 1 | BOOL | IOL7_Maint_Evts | BOOL | 278 | 6 | IO-Link channel 12: Maintenance events
| IO-Link channel 12: Wrong or missing device | 139 | 2 | 1 | 278 | 2 | BOOL | IOL7_Out_Spec_Err | BOOL | 278 | 7 | IO-Link channel 12: Out of specification error
| IO-Link channel 12: Data storage error | 139 | 3 | 1 | 278 | 3 | BOOL | IOL7_Param_Err | BOOL | 279 | 0 | IO-Link channel 12: Parameterization error
| IO-Link channel 12: Process input data invalid | 139 | 5 | 1 | 278 | 5 | BOOL | IOL7_OverTemp | BOOL | 279 | 1 | IO-Link channel 12: Overtemperature
| IO-Link channel 12: Hardware error | 139 | 4 | 1 | 278 | 4 | BOOL | IOL7_Under_LL | BOOL | 279 | 2 | IO-Link channel 12: Lower limit value underrun
| IO-Link channel 12: Maintenance events | 139 | 6 | 1 | 278 | 6 | BOOL | IOL7_Over_UL | BOOL | 279 | 3 | IO-Link channel 12: Upper limit value exceeded
| IO-Link channel 12: Out of specification error | 139 | 7 | 1 | 278 | 7 | BOOL | IOL7_V_LOW | BOOL | 279 | 4 | IO-Link channel 12: Undervoltage
| IO-Link channel 12: Parameterization error | 139 | 8 | 1 | 279 | 0 | BOOL | IOL7_V_HIGH | BOOL | 279 | 5 | IO-Link channel 12: Overvoltage
| IO-Link channel 12: Overtemperature | 139 | 9 | 1 | 279 | 1 | BOOL | IOL7_OL | BOOL | 279 | 6 | IO-Link channel 12: Overload
| IO-Link channel 12: Overtemperature | 139 | 9 | 1 | 279 | 1 | BOOL | IOL7_Cmd_Err | BOOL | 279 | 7 | IO-Link channel 12: Common error
| IO-Link channel 12: Lower limit value underrun | 139 | 10 | 1 | 279 | 2 | BOOL | IOL8_Port_Param_Err | BOOL | 280 | 1 | IO-Link channel 14: Port parameterization error
| IO-Link channel 12: Upper limit value exceeded | 139 | 11 | 1 | 279 | 3 | BOOL | IOL8_Wrong_Missing | BOOL | 280 | 2 | IO-Link channel 14: Wrong or missing device
| IO-Link channel 12: Undervoltage | 139 | 12 | 1 | 279 | 4 | BOOL | IOL8_Data_St_Err | BOOL | 280 | 3 | IO-Link channel 14: Data storage error
| IO-Link channel 12: Overvoltage | 139 | 13 | 1 | 279 | 5 | BOOL | IOL8_HW_Err | BOOL | 280 | 4 | IO-Link channel 14: Process input data invalid
| IO-Link channel 12: Overload | 139 | 14 | 1 | 279 | 6 | BOOL | IOL8_Proc_Dat_Invalid | BOOL | 280 | 5 | IO-Link channel 14: Hardware error
| IO-Link channel 12: Common error | 139 | 15 | 1 | 279 | 7 | BOOL | IOL8_Maint_Evts | BOOL | 280 | 6 | IO-Link channel 14: Maintenance events
| IO-Link channel 12: Port parameterization error | 139 | 1 | 1 | 278 | 1 | BOOL | IOL8_Out_Spec_Err | BOOL | 280 | 7 | IO-Link channel 14: Out of specification error
| IO-Link channel 14: Wrong or missing device | 140 | 2 | 1 | 280 | 2 | BOOL | IOL8_Param_Err | BOOL | 281 | 0 | IO-Link channel 14: Parameterization error
| IO-Link channel 14: Data storage error | 140 | 3 | 1 | 280 | 3 | BOOL | IOL8_OverTemp | BOOL | 281 | 1 | IO-Link channel 14: Overtemperature
| IO-Link channel 14: Process input data invalid | 140 | 5 | 1 | 280 | 5 | BOOL | IOL8_Under_LL | BOOL | 281 | 2 | IO-Link channel 14: Lower limit value underrun
| IO-Link channel 14: Hardware error | 140 | 4 | 1 | 280 | 4 | BOOL | IOL8_Over_UL | BOOL | 281 | 3 | IO-Link channel 14: Upper limit value exceeded
| IO-Link channel 14: Maintenance events | 140 | 6 | 1 | 280 | 6 | BOOL | IOL8_V_LOW | BOOL | 281 | 4 | IO-Link channel 14: Undervoltage
| IO-Link channel 14: Out of specification error | 140 | 7 | 1 | 280 | 7 | BOOL | IOL8_V_HIGH | BOOL | 281 | 5 | IO-Link channel 14: Overvoltage
| IO-Link channel 14: Parameterization error | 140 | 8 | 1 | 281 | 0 | BOOL | IOL8_OL | BOOL | 281 | 6 | IO-Link channel 14: Overload
| IO-Link channel 14: Overtemperature | 140 | 9 | 1 | 281 | 1 | BOOL | IOL8_Cmd_Err | BOOL | 281 | 7 | IO-Link channel 14: Common error
| IO-Link channel 14: Overtemperature | 140 | 9 | 1 | 281 | 1 | BOOL | IOL_Event_1_Qualifier | BYTE | 282 |  | IO-Link event 1: Qualifier
| IO-Link channel 14: Lower limit value underrun | 140 | 10 | 1 | 281 | 2 | BOOL | IOL_Event_1_Port | BYTE | 283 |  | IO-Link event 1: Port
| IO-Link channel 14: Upper limit value exceeded | 140 | 11 | 1 | 281 | 3 | BOOL | IOL_Event_1_Code | WORD | 284 |  | IO-Link event 1: Event code
| IO-Link channel 14: Undervoltage | 140 | 12 | 1 | 281 | 4 | BOOL | IOL_Event_2_Qualifier | BYTE | 286 |  | IO-Link event 1: Qualifier
| IO-Link channel 14: Overvoltage | 140 | 13 | 1 | 281 | 5 | BOOL | IOL_Event_2_Port | BYTE | 287 |  | IO-Link event 1: Port
| IO-Link channel 14: Overload | 140 | 14 | 1 | 281 | 6 | BOOL | IOL_Event_2_Code | WORD | 288 |  | IO-Link event 1: Event code
| IO-Link channel 14: Common error | 140 | 15 | 1 | 281 | 7 | BOOL | IOL_Event_3_Qualifier | BYTE | 290 |  | IO-Link event 1: Qualifier
| IO-Link channel 14: Port parameterization error | 140 | 1 | 1 | 280 | 1 | BOOL | IOL_Event_3_Port | BYTE | 291 |  | IO-Link event 1: Port
IO-Link event | IO-Link event 1: Port | 141 | 8 | 8 | 283 | 0 | BYTE | IOL_Event_3_Code | WORD | 292 |  | IO-Link event 1: Event code
| IO-Link event 1: Qualifier | 141 | 0 | 8 | 282 | 0 | BYTE | IOL_Event_4_Qualifier | BYTE | 294 |  | IO-Link event 1: Qualifier
| IO-Link event 1: Event code | 142 | 0 | 16 | 284 | 0 | WORD | IOL_Event_4_Port | BYTE | 295 |  | IO-Link event 1: Port
| IO-Link event 2: Port | 143 | 8 | 8 | 287 | 0 | BYTE | IOL_Event_4_Code | WORD | 296 |  | IO-Link event 1: Event code
| IO-Link event 2: Qualifier | 143 | 0 | 8 | 286 | 0 | BYTE | IOL_Event_5_Qualifier | BYTE | 298 |  | IO-Link event 1: Qualifier
| IO-Link event 2: Event code | 144 | 0 | 16 | 288 | 0 | WORD | IOL_Event_5_Port | BYTE | 299 |  | IO-Link event 1: Port
| IO-Link event 3: Port | 145 | 8 | 8 | 291 | 0 | BYTE | IOL_Event_5_Code | WORD | 300 |  | IO-Link event 1: Event code
| IO-Link event 3: Qualifier | 145 | 0 | 8 | 290 | 0 | BYTE | IOL_Event_6_Qualifier | BYTE | 302 |  | IO-Link event 1: Qualifier
| IO-Link event 3: Event code | 146 | 0 | 16 | 292 | 0 | WORD | IOL_Event_6_Port | BYTE | 303 |  | IO-Link event 1: Port
| IO-Link event 4: Port | 147 | 8 | 8 | 295 | 0 | BYTE | IOL_Event_6_Code | WORD | 304 |  | IO-Link event 1: Event code
| IO-Link event 4: Qualifier | 147 | 0 | 8 | 294 | 0 | BYTE | IOL_Event_7_Qualifier | BYTE | 306 |  | IO-Link event 1: Qualifier
| IO-Link event 4: Event code | 148 | 0 | 16 | 296 | 0 | WORD | IOL_Event_7_Port | BYTE | 307 |  | IO-Link event 1: Port
| IO-Link event 5: Port | 149 | 8 | 8 | 299 | 0 | BYTE | IOL_Event_7_Code | WORD | 308 |  | IO-Link event 1: Event code
| IO-Link event 5: Qualifier | 149 | 0 | 8 | 298 | 0 | BYTE | IOL_Event_8_Qualifier | BYTE | 310 |  | IO-Link event 1: Qualifier
| IO-Link event 5: Event code | 150 | 0 | 16 | 300 | 0 | WORD | IOL_Event_8_Port | BYTE | 311 |  | IO-Link event 1: Port
| IO-Link event 6: Port | 151 | 8 | 8 | 303 | 0 | BYTE | IOL_Event_8_Code | WORD | 312 |  | IO-Link event 1: Event code
| IO-Link event 6: Qualifier | 151 | 0 | 8 | 302 | 0 | BYTE | IOL_Event_9_Qualifier | BYTE | 314 |  | IO-Link event 1: Qualifier
| IO-Link event 6: Event code | 152 | 0 | 16 | 304 | 0 | WORD | IOL_Event_9_Port | BYTE | 315 |  | IO-Link event 1: Port
| IO-Link event 7: Port | 153 | 8 | 8 | 307 | 0 | BYTE | IOL_Event_9_Code | WORD | 316 |  | IO-Link event 1: Event code
| IO-Link event 7: Qualifier | 153 | 0 | 8 | 306 | 0 | BYTE | IOL_Event_10_Qualifier | BYTE | 318 |  | IO-Link event 1: Qualifier
| IO-Link event 7: Event code | 154 | 0 | 16 | 308 | 0 | WORD | IOL_Event_10_Port | BYTE | 319 |  | IO-Link event 1: Port
| IO-Link event 8: Port | 155 | 8 | 8 | 311 | 0 | BYTE | IOL_Event_10_Code | WORD | 320 |  | IO-Link event 1: Event code
| IO-Link event 8: Qualifier | 155 | 0 | 8 | 310 | 0 | BYTE | IOL_Event_11_Qualifier | BYTE | 322 |  | IO-Link event 1: Qualifier
| IO-Link event 8: Event code | 156 | 0 | 16 | 312 | 0 | WORD | IOL_Event_11_Port | BYTE | 323 |  | IO-Link event 1: Port
| IO-Link event 9: Port | 157 | 8 | 8 | 315 | 0 | BYTE | IOL_Event_11_Code | WORD | 324 |  | IO-Link event 1: Event code
| IO-Link event 9: Qualifier | 157 | 0 | 8 | 314 | 0 | BYTE | IOL_Event_12_Qualifier | BYTE | 326 |  | IO-Link event 1: Qualifier
| IO-Link event 9: Event code | 158 | 0 | 16 | 316 | 0 | WORD | IOL_Event_12_Port | BYTE | 327 |  | IO-Link event 1: Port
| IO-Link event 10: Port | 159 | 8 | 8 | 319 | 0 | BYTE | IOL_Event_12_Code | WORD | 328 |  | IO-Link event 1: Event code
| IO-Link event 10: Qualifier | 159 | 0 | 8 | 318 | 0 | BYTE | IOL_Event_13_Qualifier | BYTE | 330 |  | IO-Link event 1: Qualifier
| IO-Link event 10: Event code | 160 | 0 | 16 | 320 | 0 | WORD | IOL_Event_13_Port | BYTE | 331 |  | IO-Link event 1: Port
| IO-Link event 11: Port | 161 | 8 | 8 | 323 | 0 | BYTE | IOL_Event_13_Code | WORD | 332 |  | IO-Link event 1: Event code
| IO-Link event 11: Qualifier | 161 | 0 | 8 | 322 | 0 | BYTE | IOL_Event_14_Qualifier | BYTE | 334 |  | IO-Link event 1: Qualifier
| IO-Link event 11: Event code | 162 | 0 | 16 | 324 | 0 | WORD | IOL_Event_14_Port | BYTE | 335 |  | IO-Link event 1: Port
| IO-Link event 12: Port | 163 | 8 | 8 | 327 | 0 | BYTE | IOL_Event_14_Code | WORD | 336 |  | IO-Link event 1: Event code
| IO-Link event 12: Qualifier | 163 | 0 | 8 | 326 | 0 | BYTE | IOL_Event_15_Qualifier | BYTE | 338 |  | IO-Link event 1: Qualifier
| IO-Link event 12: Event code | 164 | 0 | 16 | 328 | 0 | WORD | IOL_Event_15_Port | BYTE | 339 |  | IO-Link event 1: Port
| IO-Link event 13: Port | 165 | 8 | 8 | 331 | 0 | BYTE | IOL_Event_15_Code | WORD | 340 |  | IO-Link event 1: Event code
| IO-Link event 13: Qualifier | 165 | 0 | 8 | 330 | 0 | BYTE | IOL_Event_16_Qualifier | BYTE | 342 |  | IO-Link event 1: Qualifier
| IO-Link event 13: Event code | 166 | 0 | 16 | 332 | 0 | WORD | IOL_Event_16_Port | BYTE | 343 |  | IO-Link event 1: Port
| IO-Link event 14: Port | 167 | 8 | 8 | 335 | 0 | BYTE | IOL_Event_16_Code | WORD | 344 |  | IO-Link event 1: Event code
| IO-Link event 14: Qualifier | 167 | 0 | 8 | 334 | 0 | BYTE
| IO-Link event 14: Event code | 168 | 0 | 16 | 336 | 0 | WORD
| IO-Link event 15: Port | 169 | 8 | 8 | 339 | 0 | BYTE
| IO-Link event 15: Qualifier | 169 | 0 | 8 | 338 | 0 | BYTE
| IO-Link event 15: Event code | 170 | 0 | 16 | 340 | 0 | WORD
| IO-Link event 16: Port | 171 | 8 | 8 | 343 | 0 | BYTE
| IO-Link event 16: Qualifier | 171 | 0 | 8 | 342 | 0 | BYTE
| IO-Link event 16: Event code | 172 | 0 | 16 | 344 | 0 | WORD

## TBEN-L4-8IOL_OUT
| Connection | Assembly Instance | Size (in words)
| Output | 104 | 131
| Description | Word Offset | Bit Offset (Word Mapping) | Bit Length | Byte Offset | Bit Offset (Byte Mapping) | Data Type | Name | Base Type | Offset Byte | Offset Bit | Comment
Basic | Port 1 - IO-Link (Channel 0): Deactivate diagnostics | 1 | 0 | 1 | 2 | 0 | BOOL | STRUCT_TBEN_Lx_8IOL_104_V1_OUT | STRUCT |  |  |  | User
| Port 2 - IO-Link (Channel 2): Deactivate diagnostics | 1 | 2 | 1 | 2 | 2 | BOOL | DxP1_OUT | BOOL | 2 | 1
| Port 3 - IO-Link (Channel 4): Deactivate diagnostics | 1 | 4 | 1 | 2 | 4 | BOOL | DxP3_OUT | BOOL | 2 | 3
| Port 4 - IO-Link (Channel 6): Deactivate diagnostics | 1 | 6 | 1 | 2 | 6 | BOOL | DxP5_OUT | BOOL | 2 | 5
| Port 5 - IO-Link (Channel 8): Deactivate diagnostics | 1 | 8 | 1 | 3 | 0 | BOOL | DxP7_OUT | BOOL | 2 | 7
| Port 6 - IO-Link (Channel 10): Deactivate diagnostics | 1 | 10 | 1 | 3 | 2 | BOOL | IOL1_W1_OUT | WORD | 4 |  | IO-Link port: Output data word 0
| Port 7 - IO-Link (Channel 12): Deactivate diagnostics | 1 | 12 | 1 | 3 | 4 | BOOL | IOL1_W2_OUT | WORD | 6 |  | IO-Link port: Output data word 1
| Port 8 - IO-Link (Channel 14): Deactivate diagnostics | 1 | 14 | 1 | 3 | 6 | BOOL | IOL1_W0_OUT | WORD | 8 |  | IO-Link port: Output data word 2
| DXP channel 1: Output value | 1 | 1 | 1 | 2 | 1 | BOOL | IOL1_W3_OUT | WORD | 10 |  | IO-Link port: Output data word 3
| DXP channel 3: Output value | 1 | 3 | 1 | 2 | 3 | BOOL | IOL1_W4_OUT | WORD | 12 |  | IO-Link port: Output data word 4
| DXP channel 5: Output value | 1 | 5 | 1 | 2 | 5 | BOOL | IOL1_W5_OUT | WORD | 14 |  | IO-Link port: Output data word 5
| DXP channel 7: Output value | 1 | 7 | 1 | 2 | 7 | BOOL | IOL1_W6_OUT | WORD | 16 |  | IO-Link port: Output data word 6
Port 1 - IO-Link (Channel 0) | IO-Link port: Output data word 0 | 2 | 0 | 16 | 4 | 0 | WORD | IOL1_W7_OUT | WORD | 18 |  | IO-Link port: Output data word 7
| IO-Link port: Output data word 1 | 3 | 0 | 16 | 6 | 0 | WORD | IOL1_W8_OUT | WORD | 20 |  | IO-Link port: Output data word 8
| IO-Link port: Output data word 2 | 4 | 0 | 16 | 8 | 0 | WORD | IOL1_W9_OUT | WORD | 22 |  | IO-Link port: Output data word 9
| IO-Link port: Output data word 3 | 5 | 0 | 16 | 10 | 0 | WORD | IOL1_W10_OUT | WORD | 24 |  | IO-Link port: Output data word 10
| IO-Link port: Output data word 4 | 6 | 0 | 16 | 12 | 0 | WORD | IOL1_W11_OUT | WORD | 26 |  | IO-Link port: Output data word 11
| IO-Link port: Output data word 5 | 7 | 0 | 16 | 14 | 0 | WORD | IOL1_W12_OUT | WORD | 28 |  | IO-Link port: Output data word 12
| IO-Link port: Output data word 6 | 8 | 0 | 16 | 16 | 0 | WORD | IOL1_W13_OUT | WORD | 30 |  | IO-Link port: Output data word 13
| IO-Link port: Output data word 7 | 9 | 0 | 16 | 18 | 0 | WORD | IOL1_W14_OUT | WORD | 32 |  | IO-Link port: Output data word 14
| IO-Link port: Output data word 8 | 10 | 0 | 16 | 20 | 0 | WORD | IOL1_W15_OUT | WORD | 34 |  | IO-Link port: Output data word 15
| IO-Link port: Output data word 9 | 11 | 0 | 16 | 22 | 0 | WORD | IOL2_W0_OUT | WORD | 36 |  | IO-Link port: Output data word 0
| IO-Link port: Output data word 10 | 12 | 0 | 16 | 24 | 0 | WORD | IOL2_W1_OUT | WORD | 38 |  | IO-Link port: Output data word 1
| IO-Link port: Output data word 11 | 13 | 0 | 16 | 26 | 0 | WORD | IOL2_W2_OUT | WORD | 40 |  | IO-Link port: Output data word 2
| IO-Link port: Output data word 12 | 14 | 0 | 16 | 28 | 0 | WORD | IOL2_W3_OUT | WORD | 42 |  | IO-Link port: Output data word 3
| IO-Link port: Output data word 13 | 15 | 0 | 16 | 30 | 0 | WORD | IOL2_W4_OUT | WORD | 44 |  | IO-Link port: Output data word 4
| IO-Link port: Output data word 14 | 16 | 0 | 16 | 32 | 0 | WORD | IOL2_W5_OUT | WORD | 46 |  | IO-Link port: Output data word 5
| IO-Link port: Output data word 15 | 17 | 0 | 16 | 34 | 0 | WORD | IOL2_W6_OUT | WORD | 48 |  | IO-Link port: Output data word 6
Port 2 - IO-Link (Channel 2) | IO-Link port: Output data word 0 | 18 | 0 | 16 | 36 | 0 | WORD | IOL2_W7_OUT | WORD | 50 |  | IO-Link port: Output data word 7
| IO-Link port: Output data word 1 | 19 | 0 | 16 | 38 | 0 | WORD | IOL2_W8_OUT | WORD | 52 |  | IO-Link port: Output data word 8
| IO-Link port: Output data word 2 | 20 | 0 | 16 | 40 | 0 | WORD | IOL2_W9_OUT | WORD | 54 |  | IO-Link port: Output data word 9
| IO-Link port: Output data word 3 | 21 | 0 | 16 | 42 | 0 | WORD | IOL2_W10_OUT | WORD | 56 |  | IO-Link port: Output data word 10
| IO-Link port: Output data word 4 | 22 | 0 | 16 | 44 | 0 | WORD | IOL2_W11_OUT | WORD | 58 |  | IO-Link port: Output data word 11
| IO-Link port: Output data word 5 | 23 | 0 | 16 | 46 | 0 | WORD | IOL2_W12_OUT | WORD | 60 |  | IO-Link port: Output data word 12
| IO-Link port: Output data word 6 | 24 | 0 | 16 | 48 | 0 | WORD | IOL2_W13_OUT | WORD | 62 |  | IO-Link port: Output data word 13
| IO-Link port: Output data word 7 | 25 | 0 | 16 | 50 | 0 | WORD | IOL2_W14_OUT | WORD | 64 |  | IO-Link port: Output data word 14
| IO-Link port: Output data word 8 | 26 | 0 | 16 | 52 | 0 | WORD | IOL2_W15_OUT | WORD | 66 |  | IO-Link port: Output data word 15
| IO-Link port: Output data word 9 | 27 | 0 | 16 | 54 | 0 | WORD | IOL3_W0_OUT | WORD | 68 |  | IO-Link port: Output data word 0
| IO-Link port: Output data word 10 | 28 | 0 | 16 | 56 | 0 | WORD | IOL3_W1_OUT | WORD | 70 |  | IO-Link port: Output data word 1
| IO-Link port: Output data word 11 | 29 | 0 | 16 | 58 | 0 | WORD | IOL3_W2_OUT | WORD | 72 |  | IO-Link port: Output data word 2
| IO-Link port: Output data word 12 | 30 | 0 | 16 | 60 | 0 | WORD | IOL3_W3_OUT | WORD | 74 |  | IO-Link port: Output data word 3
| IO-Link port: Output data word 13 | 31 | 0 | 16 | 62 | 0 | WORD | IOL3_W4_OUT | WORD | 76 |  | IO-Link port: Output data word 4
| IO-Link port: Output data word 14 | 32 | 0 | 16 | 64 | 0 | WORD | IOL3_W5_OUT | WORD | 78 |  | IO-Link port: Output data word 5
| IO-Link port: Output data word 15 | 33 | 0 | 16 | 66 | 0 | WORD | IOL3_W6_OUT | WORD | 80 |  | IO-Link port: Output data word 6
Port 3 - IO-Link (Channel 4) | IO-Link port: Output data word 0 | 34 | 0 | 16 | 68 | 0 | WORD | IOL3_W7_OUT | WORD | 82 |  | IO-Link port: Output data word 7
| IO-Link port: Output data word 1 | 35 | 0 | 16 | 70 | 0 | WORD | IOL3_W8_OUT | WORD | 84 |  | IO-Link port: Output data word 8
| IO-Link port: Output data word 2 | 36 | 0 | 16 | 72 | 0 | WORD | IOL3_W9_OUT | WORD | 86 |  | IO-Link port: Output data word 9
| IO-Link port: Output data word 3 | 37 | 0 | 16 | 74 | 0 | WORD | IOL3_W10_OUT | WORD | 88 |  | IO-Link port: Output data word 10
| IO-Link port: Output data word 4 | 38 | 0 | 16 | 76 | 0 | WORD | IOL3_W11_OUT | WORD | 90 |  | IO-Link port: Output data word 11
| IO-Link port: Output data word 5 | 39 | 0 | 16 | 78 | 0 | WORD | IOL3_W12_OUT | WORD | 92 |  | IO-Link port: Output data word 12
| IO-Link port: Output data word 6 | 40 | 0 | 16 | 80 | 0 | WORD | IOL3_W13_OUT | WORD | 94 |  | IO-Link port: Output data word 13
| IO-Link port: Output data word 7 | 41 | 0 | 16 | 82 | 0 | WORD | IOL3_W14_OUT | WORD | 96 |  | IO-Link port: Output data word 14
| IO-Link port: Output data word 8 | 42 | 0 | 16 | 84 | 0 | WORD | IOL3_W15_OUT | WORD | 98 |  | IO-Link port: Output data word 15
| IO-Link port: Output data word 9 | 43 | 0 | 16 | 86 | 0 | WORD | IOL4_W0_OUT | WORD | 100 |  | IO-Link port: Output data word 0
| IO-Link port: Output data word 10 | 44 | 0 | 16 | 88 | 0 | WORD | IOL4_W1_OUT | WORD | 102 |  | IO-Link port: Output data word 1
| IO-Link port: Output data word 11 | 45 | 0 | 16 | 90 | 0 | WORD | IOL4_W2_OUT | WORD | 104 |  | IO-Link port: Output data word 2
| IO-Link port: Output data word 12 | 46 | 0 | 16 | 92 | 0 | WORD | IOL4_W3_OUT | WORD | 106 |  | IO-Link port: Output data word 3
| IO-Link port: Output data word 13 | 47 | 0 | 16 | 94 | 0 | WORD | IOL4_W4_OUT | WORD | 108 |  | IO-Link port: Output data word 4
| IO-Link port: Output data word 14 | 48 | 0 | 16 | 96 | 0 | WORD | IOL4_W5_OUT | WORD | 110 |  | IO-Link port: Output data word 5
| IO-Link port: Output data word 15 | 49 | 0 | 16 | 98 | 0 | WORD | IOL4_W6_OUT | WORD | 112 |  | IO-Link port: Output data word 6
Port 4 - IO-Link (Channel 6) | IO-Link port: Output data word 0 | 50 | 0 | 16 | 100 | 0 | WORD | IOL4_W7_OUT | WORD | 114 |  | IO-Link port: Output data word 7
| IO-Link port: Output data word 1 | 51 | 0 | 16 | 102 | 0 | WORD | IOL4_W8_OUT | WORD | 116 |  | IO-Link port: Output data word 8
| IO-Link port: Output data word 2 | 52 | 0 | 16 | 104 | 0 | WORD | IOL4_W9_OUT | WORD | 118 |  | IO-Link port: Output data word 9
| IO-Link port: Output data word 3 | 53 | 0 | 16 | 106 | 0 | WORD | IOL4_W10_OUT | WORD | 120 |  | IO-Link port: Output data word 10
| IO-Link port: Output data word 4 | 54 | 0 | 16 | 108 | 0 | WORD | IOL4_W11_OUT | WORD | 122 |  | IO-Link port: Output data word 11
| IO-Link port: Output data word 5 | 55 | 0 | 16 | 110 | 0 | WORD | IOL4_W12_OUT | WORD | 124 |  | IO-Link port: Output data word 12
| IO-Link port: Output data word 6 | 56 | 0 | 16 | 112 | 0 | WORD | IOL4_W13_OUT | WORD | 126 |  | IO-Link port: Output data word 13
| IO-Link port: Output data word 7 | 57 | 0 | 16 | 114 | 0 | WORD | IOL4_W14_OUT | WORD | 128 |  | IO-Link port: Output data word 14
| IO-Link port: Output data word 8 | 58 | 0 | 16 | 116 | 0 | WORD | IOL4_W15_OUT | WORD | 130 |  | IO-Link port: Output data word 15
| IO-Link port: Output data word 9 | 59 | 0 | 16 | 118 | 0 | WORD | IOL5_W0_OUT | WORD | 132 |  | IO-Link port: Output data word 0
| IO-Link port: Output data word 10 | 60 | 0 | 16 | 120 | 0 | WORD | IOL5_W1_OUT | WORD | 134 |  | IO-Link port: Output data word 1
| IO-Link port: Output data word 11 | 61 | 0 | 16 | 122 | 0 | WORD | IOL5_W2_OUT | WORD | 136 |  | IO-Link port: Output data word 2
| IO-Link port: Output data word 12 | 62 | 0 | 16 | 124 | 0 | WORD | IOL5_W3_OUT | WORD | 138 |  | IO-Link port: Output data word 3
| IO-Link port: Output data word 13 | 63 | 0 | 16 | 126 | 0 | WORD | IOL5_W4_OUT | WORD | 140 |  | IO-Link port: Output data word 4
| IO-Link port: Output data word 14 | 64 | 0 | 16 | 128 | 0 | WORD | IOL5_W5_OUT | WORD | 142 |  | IO-Link port: Output data word 5
| IO-Link port: Output data word 15 | 65 | 0 | 16 | 130 | 0 | WORD | IOL5_W6_OUT | WORD | 144 |  | IO-Link port: Output data word 6
Port 5 - IO-Link (Channel 8) | IO-Link port: Output data word 0 | 66 | 0 | 16 | 132 | 0 | WORD | IOL5_W7_OUT | WORD | 146 |  | IO-Link port: Output data word 7
| IO-Link port: Output data word 1 | 67 | 0 | 16 | 134 | 0 | WORD | IOL5_W8_OUT | WORD | 148 |  | IO-Link port: Output data word 8
| IO-Link port: Output data word 2 | 68 | 0 | 16 | 136 | 0 | WORD | IOL5_W9_OUT | WORD | 150 |  | IO-Link port: Output data word 9
| IO-Link port: Output data word 3 | 69 | 0 | 16 | 138 | 0 | WORD | IOL5_W10_OUT | WORD | 152 |  | IO-Link port: Output data word 10
| IO-Link port: Output data word 4 | 70 | 0 | 16 | 140 | 0 | WORD | IOL5_W11_OUT | WORD | 154 |  | IO-Link port: Output data word 11
| IO-Link port: Output data word 5 | 71 | 0 | 16 | 142 | 0 | WORD | IOL5_W12_OUT | WORD | 156 |  | IO-Link port: Output data word 12
| IO-Link port: Output data word 6 | 72 | 0 | 16 | 144 | 0 | WORD | IOL5_W13_OUT | WORD | 158 |  | IO-Link port: Output data word 13
| IO-Link port: Output data word 7 | 73 | 0 | 16 | 146 | 0 | WORD | IOL5_W14_OUT | WORD | 160 |  | IO-Link port: Output data word 14
| IO-Link port: Output data word 8 | 74 | 0 | 16 | 148 | 0 | WORD | IOL5_W15_OUT | WORD | 162 |  | IO-Link port: Output data word 15
| IO-Link port: Output data word 9 | 75 | 0 | 16 | 150 | 0 | WORD | IOL6_W0_OUT | WORD | 164 |  | IO-Link port: Output data word 0
| IO-Link port: Output data word 10 | 76 | 0 | 16 | 152 | 0 | WORD | IOL6_W1_OUT | WORD | 166 |  | IO-Link port: Output data word 1
| IO-Link port: Output data word 11 | 77 | 0 | 16 | 154 | 0 | WORD | IOL6_W2_OUT | WORD | 168 |  | IO-Link port: Output data word 2
| IO-Link port: Output data word 12 | 78 | 0 | 16 | 156 | 0 | WORD | IOL6_W3_OUT | WORD | 170 |  | IO-Link port: Output data word 3
| IO-Link port: Output data word 13 | 79 | 0 | 16 | 158 | 0 | WORD | IOL6_W4_OUT | WORD | 172 |  | IO-Link port: Output data word 4
| IO-Link port: Output data word 14 | 80 | 0 | 16 | 160 | 0 | WORD | IOL6_W5_OUT | WORD | 174 |  | IO-Link port: Output data word 5
| IO-Link port: Output data word 15 | 81 | 0 | 16 | 162 | 0 | WORD | IOL6_W6_OUT | WORD | 176 |  | IO-Link port: Output data word 6
Port 6 - IO-Link (Channel 10) | IO-Link port: Output data word 0 | 82 | 0 | 16 | 164 | 0 | WORD | IOL6_W7_OUT | WORD | 178 |  | IO-Link port: Output data word 7
| IO-Link port: Output data word 1 | 83 | 0 | 16 | 166 | 0 | WORD | IOL6_W8_OUT | WORD | 180 |  | IO-Link port: Output data word 8
| IO-Link port: Output data word 2 | 84 | 0 | 16 | 168 | 0 | WORD | IOL6_W9_OUT | WORD | 182 |  | IO-Link port: Output data word 9
| IO-Link port: Output data word 3 | 85 | 0 | 16 | 170 | 0 | WORD | IOL6_W10_OUT | WORD | 184 |  | IO-Link port: Output data word 10
| IO-Link port: Output data word 4 | 86 | 0 | 16 | 172 | 0 | WORD | IOL6_W11_OUT | WORD | 186 |  | IO-Link port: Output data word 11
| IO-Link port: Output data word 5 | 87 | 0 | 16 | 174 | 0 | WORD | IOL6_W12_OUT | WORD | 188 |  | IO-Link port: Output data word 12
| IO-Link port: Output data word 6 | 88 | 0 | 16 | 176 | 0 | WORD | IOL6_W13_OUT | WORD | 190 |  | IO-Link port: Output data word 13
| IO-Link port: Output data word 7 | 89 | 0 | 16 | 178 | 0 | WORD | IOL6_W14_OUT | WORD | 192 |  | IO-Link port: Output data word 14
| IO-Link port: Output data word 8 | 90 | 0 | 16 | 180 | 0 | WORD | IOL6_W15_OUT | WORD | 194 |  | IO-Link port: Output data word 15
| IO-Link port: Output data word 9 | 91 | 0 | 16 | 182 | 0 | WORD | IOL7_W0_OUT | WORD | 196 |  | IO-Link port: Output data word 0
| IO-Link port: Output data word 10 | 92 | 0 | 16 | 184 | 0 | WORD | IOL7_W1_OUT | WORD | 198 |  | IO-Link port: Output data word 1
| IO-Link port: Output data word 11 | 93 | 0 | 16 | 186 | 0 | WORD | IOL7_W2_OUT | WORD | 200 |  | IO-Link port: Output data word 2
| IO-Link port: Output data word 12 | 94 | 0 | 16 | 188 | 0 | WORD | IOL7_W3_OUT | WORD | 202 |  | IO-Link port: Output data word 3
| IO-Link port: Output data word 13 | 95 | 0 | 16 | 190 | 0 | WORD | IOL7_W4_OUT | WORD | 204 |  | IO-Link port: Output data word 4
| IO-Link port: Output data word 14 | 96 | 0 | 16 | 192 | 0 | WORD | IOL7_W5_OUT | WORD | 206 |  | IO-Link port: Output data word 5
| IO-Link port: Output data word 15 | 97 | 0 | 16 | 194 | 0 | WORD | IOL7_W6_OUT | WORD | 208 |  | IO-Link port: Output data word 6
Port 7 - IO-Link (Channel 12) | IO-Link port: Output data word 0 | 98 | 0 | 16 | 196 | 0 | WORD | IOL7_W7_OUT | WORD | 210 |  | IO-Link port: Output data word 7
| IO-Link port: Output data word 1 | 99 | 0 | 16 | 198 | 0 | WORD | IOL7_W8_OUT | WORD | 212 |  | IO-Link port: Output data word 8
| IO-Link port: Output data word 2 | 100 | 0 | 16 | 200 | 0 | WORD | IOL7_W9_OUT | WORD | 214 |  | IO-Link port: Output data word 9
| IO-Link port: Output data word 3 | 101 | 0 | 16 | 202 | 0 | WORD | IOL7_W10_OUT | WORD | 216 |  | IO-Link port: Output data word 10
| IO-Link port: Output data word 4 | 102 | 0 | 16 | 204 | 0 | WORD | IOL7_W11_OUT | WORD | 218 |  | IO-Link port: Output data word 11
| IO-Link port: Output data word 5 | 103 | 0 | 16 | 206 | 0 | WORD | IOL7_W12_OUT | WORD | 220 |  | IO-Link port: Output data word 12
| IO-Link port: Output data word 6 | 104 | 0 | 16 | 208 | 0 | WORD | IOL7_W13_OUT | WORD | 222 |  | IO-Link port: Output data word 13
| IO-Link port: Output data word 7 | 105 | 0 | 16 | 210 | 0 | WORD | IOL7_W14_OUT | WORD | 224 |  | IO-Link port: Output data word 14
| IO-Link port: Output data word 8 | 106 | 0 | 16 | 212 | 0 | WORD | IOL7_W15_OUT | WORD | 226 |  | IO-Link port: Output data word 15
| IO-Link port: Output data word 9 | 107 | 0 | 16 | 214 | 0 | WORD | IOL8_W0_OUT | WORD | 228 |  | IO-Link port: Output data word 0
| IO-Link port: Output data word 10 | 108 | 0 | 16 | 216 | 0 | WORD | IOL8_W1_OUT | WORD | 230 |  | IO-Link port: Output data word 1
| IO-Link port: Output data word 11 | 109 | 0 | 16 | 218 | 0 | WORD | IOL8_W2_OUT | WORD | 232 |  | IO-Link port: Output data word 2
| IO-Link port: Output data word 12 | 110 | 0 | 16 | 220 | 0 | WORD | IOL8_W3_OUT | WORD | 234 |  | IO-Link port: Output data word 3
| IO-Link port: Output data word 13 | 111 | 0 | 16 | 222 | 0 | WORD | IOL8_W4_OUT | WORD | 236 |  | IO-Link port: Output data word 4
| IO-Link port: Output data word 14 | 112 | 0 | 16 | 224 | 0 | WORD | IOL8_W5_OUT | WORD | 238 |  | IO-Link port: Output data word 5
| IO-Link port: Output data word 15 | 113 | 0 | 16 | 226 | 0 | WORD | IOL8_W6_OUT | WORD | 240 |  | IO-Link port: Output data word 6
Port 8 - IO-Link (Channel 14) | IO-Link port: Output data word 0 | 114 | 0 | 16 | 228 | 0 | WORD | IOL8_W7_OUT | WORD | 242 |  | IO-Link port: Output data word 7
| IO-Link port: Output data word 1 | 115 | 0 | 16 | 230 | 0 | WORD | IOL8_W8_OUT | WORD | 244 |  | IO-Link port: Output data word 8
| IO-Link port: Output data word 2 | 116 | 0 | 16 | 232 | 0 | WORD | IOL8_W9_OUT | WORD | 246 |  | IO-Link port: Output data word 9
| IO-Link port: Output data word 3 | 117 | 0 | 16 | 234 | 0 | WORD | IOL8_W10_OUT | WORD | 248 |  | IO-Link port: Output data word 10
| IO-Link port: Output data word 4 | 118 | 0 | 16 | 236 | 0 | WORD | IOL8_W11_OUT | WORD | 250 |  | IO-Link port: Output data word 11
| IO-Link port: Output data word 5 | 119 | 0 | 16 | 238 | 0 | WORD | IOL8_W12_OUT | WORD | 252 |  | IO-Link port: Output data word 12
| IO-Link port: Output data word 6 | 120 | 0 | 16 | 240 | 0 | WORD | IOL8_W13_OUT | WORD | 254 |  | IO-Link port: Output data word 13
| IO-Link port: Output data word 7 | 121 | 0 | 16 | 242 | 0 | WORD | IOL8_W14_OUT | WORD | 256 |  | IO-Link port: Output data word 14
| IO-Link port: Output data word 8 | 122 | 0 | 16 | 244 | 0 | WORD | IOL8_W15_OUT | WORD | 258 |  | IO-Link port: Output data word 15
| IO-Link port: Output data word 9 | 123 | 0 | 16 | 246 | 0 | WORD | Pin1_C0_VAUX1_Ctrl | BOOL | 260 | 0 | VAUX control: VAUX1 Pin1 C0 (Ch0/1)
| IO-Link port: Output data word 10 | 124 | 0 | 16 | 248 | 0 | WORD | Pin1_C1_VAUX1_Ctrl | BOOL | 260 | 1 | VAUX control: VAUX1 Pin1 C1 (Ch2/3)
| IO-Link port: Output data word 11 | 125 | 0 | 16 | 250 | 0 | WORD | Pin1_C2_VAUX1_Ctrl | BOOL | 260 | 2 | VAUX control: VAUX1 Pin1 C2 (Ch4/5)
| IO-Link port: Output data word 12 | 126 | 0 | 16 | 252 | 0 | WORD | Pin1_C3_VAUX1_Ctrl | BOOL | 260 | 3 | VAUX control: VAUX1 Pin1 C3 (Ch6/7)
| IO-Link port: Output data word 13 | 127 | 0 | 16 | 254 | 0 | WORD | Pin1_C4_VAUX1_Ctrl | BOOL | 260 | 4 | VAUX control: VAUX1 Pin1 C4 (Ch8)
| IO-Link port: Output data word 14 | 128 | 0 | 16 | 256 | 0 | WORD | Pin1_C5_VAUX1_Ctrl | BOOL | 260 | 5 | VAUX control: VAUX1 Pin1 C5 (Ch10)
| IO-Link port: Output data word 15 | 129 | 0 | 16 | 258 | 0 | WORD | Pin1_C6_VAUX1_Ctrl | BOOL | 260 | 6 | VAUX control: VAUX1 Pin1 C6 (Ch12)
VAUX control | VAUX control: VAUX1 Pin1 C0 (Ch0/1) | 130 | 0 | 1 | 260 | 0 | BOOL | Pin1_C7_VAUX1_Ctrl | BOOL | 260 | 7 | VAUX control: VAUX1 Pin1 C7 (Ch14)
| VAUX control: VAUX1 Pin1 C1 (Ch2/3) | 130 | 1 | 1 | 260 | 1 | BOOL | Pin2_C4_VAUX2_Ctrl | BOOL | 261 | 4 | VAUX control: VAUX2 Pin2 C4 (Ch9)
| VAUX control: VAUX1 Pin1 C2 (Ch4/5) | 130 | 2 | 1 | 260 | 2 | BOOL | Pin2_C5_VAUX2_Ctrl | BOOL | 261 | 5 | VAUX control: VAUX2 Pin2 C5 (Ch11)
| VAUX control: VAUX1 Pin1 C3 (Ch6/7) | 130 | 3 | 1 | 260 | 3 | BOOL | Pin2_C6_VAUX2_Ctrl | BOOL | 261 | 6 | VAUX control: VAUX2 Pin2 C6 (Ch13)
| VAUX control: VAUX1 Pin1 C4 (Ch8) | 130 | 4 | 1 | 260 | 4 | BOOL | Pin2_C7_VAUX2_Ctrl | BOOL | 261 | 7 | VAUX control: VAUX2 Pin2 C7 (Ch15)
| VAUX control: VAUX2 Pin2 C4 (Ch9) | 130 | 12 | 1 | 261 | 4 | BOOL
| VAUX control: VAUX1 Pin1 C5 (Ch10) | 130 | 5 | 1 | 260 | 5 | BOOL
| VAUX control: VAUX2 Pin2 C5 (Ch11) | 130 | 13 | 1 | 261 | 5 | BOOL
| VAUX control: VAUX1 Pin1 C6 (Ch12) | 130 | 6 | 1 | 260 | 6 | BOOL
| VAUX control: VAUX2 Pin2 C6 (Ch13) | 130 | 14 | 1 | 261 | 6 | BOOL
| VAUX control: VAUX1 Pin1 C7 (Ch14) | 130 | 7 | 1 | 260 | 7 | BOOL
| VAUX control: VAUX2 Pin2 C7 (Ch15) | 130 | 15 | 1 | 261 | 7 | BOOL

## Misc
WORD 0 | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | WORD | 0 | 0 | BYTE
BYTE 1, 0 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |  | 0 | 1
| 1 (HI) | [7 empty] | 0 (LOW) | [8 empty] | 1 | 2
[18 empty] | 1 | 3
[18 empty] | 2 | 4
[18 empty] | 2 | 5
[18 empty] | 3 | 6
[18 empty] | 3 | 7
[18 empty] | 4 | 8
[18 empty] | 4 | 9
[18 empty] | 5 | 10
[18 empty] | 5 | 11
[18 empty] | 6 | 12
[18 empty] | 6 | 13
[18 empty] | 7 | 14
[18 empty] | 7 | 15
[18 empty] | 8 | 16
[18 empty] | 8 | 17
[18 empty] | 9 | 18
[18 empty] | 9 | 19